## Sheet2
6393 Powers Ave-Jacksonville, Fl 32217
customerservice@solerpalau-usa.com
STATIC PRESSURE CALCULATOR
TO FIND DUCT DIAMETER AND FRICTION LOSS |  |  |  |  | TO FIND DUCT DIAMETER AND DUCT VELOCITY |  |  |  |  | TO FIND DUCT VELOCITY AND FRICTION LOSS
Enter Velocity, Air Flow & Length |  |  |  |  | Enter Friction Loss, Airflow & Length |  |  |  |  | Enter Friction Loss, Airflow & Length
Available Pressure - (Inches W.C.)
|  | Duct Velocity (FPM) |  | 1300 |  |  |  |  | 0.23 |  |  | Duct Diameter Round (inches) | 12
|  | Duct Airflow (CFM) |  | 1000 |  |  |  | Duct Airflow (CFM) | 1000 |  |  | Duct Airflow (CFM) | 1000
|  | Duct Length (Feet) |  | 100 |  |  |  | Duct Length (Feet) | 100 |  |  | Duct Length (Feet) | 100
Enter Number of Bends |  |  |  |  | Enter Number of Bends |  |  |  |  | Enter Number of Bends
|  | 45º Bends (QTY) |  | 0 |  |  |  | 45º Bends (QTY) | 0 |  |  | 45º Bends (QTY) | 2
|  | 90º Bends (QTY) |  | 0 |  |  |  | 90º Bends (QTY) | 0 |  |  | 90º Bends (QTY) | 1
|  | 180º Offset (QTY) |  | 0 |  |  |  | 180º Offset (QTY) | 0 |  |  | 180º Offset (QTY) | 0
Results |  |  |  |  | Results |  |  |  |  | Results
|  | Duct Diameter (in) |  | 11.9 |  |  |  | Duct Diameter (in) | 11.8 |  |  | Duct Velocity (FPM) | 1273.8854
Friction Loss - (Inches W.C.)
| Friction Loss - (Inches W.C.) |  |  | 0.22611 |  |  |  | Duct Velocity (FPM) | 1317.4339 |  |  |  | 0.25964
TO FIND AIR MIXTURE |  |  |  |  | TO FIND EQUIVALENT RECTANGULAR DUCT |  |  |  |  | TO FIND EQUIVALENT ROUND DUCT
[5 empty] | Enter Diameter |  |  |  |  | Enter Height
|  | First Airstream | [5 empty] | Round Duct Diameter (in) | 24 |  |  | Rectangular Duct Height (in) | 20
| 0 | CFM |  | 0
| 0 | Temp, deg. F |  | 0 | Enter Desired Height |  |  |  |  | Enter Width
| 0 | Humidity, Gr/Lb |  | 0 |  |  |  | Rectangular Duct Height (in) | 24 |  |  | Rectangular Duct Width (in) | 20
|  | Second Airstream |  |  | Results |  | rounded to nearest inch |  |  | Results |  | rounded to nearest inch
| 0 | CFM |  | 0 |  |  |  | Rectangular Duct Width (in) | 19 |  |  | Round Duct Diameter (in) | 23
| 0 | Temp, deg. F |  | 0
| 0 | Humidity, Gr/Lb |  | 0 | APPROXIMATE DYNAMIC |  |  |  |  | MAXIMUM RECOMMENDED
[5 empty] | LOSS COEFFICIENTS |  |  |  |  | SUPPLY VELOCITY
|  | Mixture Results | [9 empty] | Main Duct | Branch
| 0 | CFM |  | 0
| 0 | Temp, deg. F |  | 0 | [5 empty] | Residential |  | 900 fpm | 600 fpm
| 0 | Humidity, Gr/Lb |  | 0
[10 empty] | Commericial |  | 1,300 fpm | 900 fpm
[10 empty] | Industrial |  | 1,800 fpm | 1,000 fpm